## Slide 1: sdmay19-17: Burns and McDonnell Substation Design
Tom Kelly, Connor Mislivec, Jake Heiller, Rebecca Franzen,
Wilson Pietruszewski, Riley O’Donnell, Nicolaus Cory

## Slide 2: Client Overview
Engineer-architect-contractor consulting firm
Headquartered in Kansas City, Missouri

## Slide 3: Problem Statement
General problem
  High voltage distribution is unsafe
  Unable to transmit power long distances
Our solution
  Design 138/69 kV greenfield substation
  Regulate voltage levels in/out
  Ring bus configuration
http://gannettfleming.com/Projects/2015/10/19/11/29/mill-electrical-substation-upgrade

## Slide 4: Functional Requirements
Site Design & Substation Layout
Ground Grid & Lightning Protection
125VDC Station Battery Design
AC Study
Relaying & Controls
  One-line
  Breaker Schematics
  Transformer Schematics
  Line Differential Schematics

## Slide 5: Technical/Other Constraints/Considerations
Three 138 kV Circuit Breakers
One 69 kV Circuit Breaker
One 138/69 kV Transformer
Ring Bus Configuration
Future “Breaker-and-a-half” Scheme
Two transmission lines entering/exiting substation
Grounding System withstand 21 kA Fault Current
Site Size of 400’ x 400’
http://eblogbd.com/detils-air-insulated-substations-bus-switching-configurations/

## Slide 6: Semester 1
3 deliverables
  Grounding design- November 2
  Lightning Protection Design- November 2
  Physical Design- November 30

## Slide 7: Semester 2
2 deliverables
  AC/DC Studies- March 1
  Controls and NIA- April 12

## Slide 8: QC Process (Testing)
Q1 Review: Independent evaluation of completing initial planning and preparation activities, setting study objectives, and/or conceptual design activities. Performed by a peer reviewer or review team
Q2 Review: Independent evaluation of completing preliminary project activities. Includes written design basis for design projects and study/analysis data for report projects. Performed by a peer reviewer or review team.
Q3 Review: Final checking of design documents. Performed by designer.
Q4 Review: Peer review of reports and design documents. Performed by peer reviewer or review team.
Q5 Review: Review of complete design, procurement, and/or construction packages. Performed by review team.
Q6 Review: Review of complete design, procurement, and/or construction packages. Performed by Burns and McDonnell engineer.

## Slide 9: One-Line Diagram

## Slide 10: Methodology - Overview
Determine all the Protection Schemes for the Substation Equipment
Determine the appropriate device functions
Adhere to the protection requirement document and show the connections between the relays, transformers, breakers, and other equipment
Review the one-line with the other group members and the client to ensure that all the protection schemes are being implemented and the connections are shown correctly

## Slide 12: Drafting
Connect all the appropriate equipment according to the protection requirements document and the protection schemes
Converse with client on accuracy and standards that are being used

## Slide 13: Completed One-Line

## Slide 14: Transformer Schematics

## Slide 15: Methodology- Overview
DC transformer schematics
  Determined necessary inputs and outputs on protection document
  Verified protection document and one-line matched
  Determined lockout relay output contact assignments
  Drafting
  QC check by other members of the group
  Send to client to receive feedback
  Modify and finalize

## Slide 16: Completed One-Line

## Slide 17: Inputs and Outputs on Protection Document

## Slide 18: Drafting of DC Schematic

## Slide 19: Lockout Relay

## Slide 20: Completed Example (SEL 387)

## Slide 21: Methodology- Overview
AC transformer schematics
  Determine CTs from one-line
  QC’d CTs with protection document
  Drafting
  QC check by other members of the group
  Sent to client to receive feedback
  Modify and finalize

## Slide 22: Completed Example (SEL-387)

## Slide 23: Completed Example (SEL-387)

## Slide 24: Completed AC Schematic

## Slide 26: DC Study

## Slide 27: Task and Data Provided by the Client
125V DC system.
Design to 1.75Vdc per cell. This equate to 105V on a 60 cell system.
Design based on an 8-hour duty cycle.
Design for a three phase, three wire 120/240 V system coming of the tertiary winding of the main substation transformer.
Choice of battery: Enesys CC-M Lead Acid Batteries

## Slide 28: Methodology
Compile list of DC load elements and their respective amp draw levels
Create duty cycle diagram to determine battery set rating necessary
Determine worst case lockout scenario and amp draw
Calculate Battery Size
Calculate Battery Charger Size

## Slide 29: Compile list of DC load elements and their respective amp draw levels

## Slide 30: Create duty cycle diagram to determine battery set rating necessary

## Slide 32: References
Burns & McDonnell Iowa State Senior Design Project 2018-2019 Protection Requirements Document. 24 Mar 2019
Burns & McDonnell One-Line Example Drawing. 24 Mar 2019
ANSI Code Table. 24 Mar 2019
Burns & McDonnell One-Line Example Sketch. 24 Mar 2019
IEEE Standard 3001.2-2017
Design Guide for Rural Substations, Section 12: Protective Relaying. 24 Mar 2019
IEEE 485-2010: IEEE Recommended Practice for Sizing Lead-Acid Batteries for Stationary Applications